Clay County Environmental Health

Waste Water Construction Inspection

Owner ______________________________________ Address __________________________

City ______________________________ State _________________ Zip Code _____________

Permit No. ____________________ Site Address _____________________________________

Pre-construction Inspection

Inspected by ___________________________________ Date ___________________________

Approved _____________________________ Not Approved ____________________________

Construction Inspection

Inspected by ___________________________________ Date ___________________________

Approved ______________________________ Not Approved ___________________________

Contractor ____________________________________________________________________

# Pre-Construction Inspection - Location

| Description | Not Applicable | Meets Standard | Does Not Meet Standard | Notes |
| --- | --- | --- | --- | --- |
| Topography |  |  |  |  |
| Drainage Ways |  |  |  |  |
| Terraces |  |  |  |  |
| Floodplain |  |  |  |  |
| Percent of Land Slope |  |  |  |  |
| Location of Property Lines |  |  |  |  |
| Location of Easements |  |  |  |  |
| Buried Utilities |  |  |  |  |
| Existing & Proposed Tile Lines |  |  |  |  |
| Existing, Proposed and Abandoned Water Wells |  |  |  |  |
| Available Area for Installation |  |  |  |  |
| Evidence of Unstable Ground |  |  |  |  |
| Alteration of Existing Soil Profile |  |  |  |  |
| Soil Analysis |  |  |  |  |
| Percolation Tests |  |  |  |  |
| Minimum Distances |  |  |  |  |

Construction Inspection – Building to Primary Treatment Unit

| Description | Not Applicable | Meets Standard | Does Not Meet Standard | Notes |
| --- | --- | --- | --- | --- |
| Schedule 40 Plastic Pipe |  |  |  |  |
| Not less than 4” in diameter |  |  |  |  |
| Grade – 4” = 12” per 100’ and 6” = 8” per 100’ |  |  |  |  |
| Cleanout where the line leaves the building & every 100’ |  |  |  |  |
| Cleanout at any change of direction exceeding 45 degrees |  |  |  |  |

Construction Inspection – Primary Treatment

| Description | Not Applicable | Meets Standard | Does Not Meet Standard | Notes |
| --- | --- | --- | --- | --- |
| Easement |  |  |  |  |
| No chemicals, grease, roof drains, foundation drains or area drains |  |  |  |  |
| Capacity – See 69.5(2) a. |  |  |  |  |
| Fill soil – level, will not settle |  |  |  |  |
| Two compartments |  |  |  |  |
| Inlet/outlet – inlet shall be 2” to 4” higher than outlet pipe |  |  |  |  |
| Baffles – 4” schedule 40 plastic pipe |  |  |  |  |
| Access – Must be provided to all part of tank at least 18” or single opening of 24” in center of tank allowing access to both compartment with two smaller openings at least 6” over both inlet & outlet |  |  |  |  |
| Riser – More than 12” below finished ground a riser at least 24” must be installed over each manhole of 18” or more to bring the top of manhole lids within 6” of finished ground surface |  |  |  |  |
| Tank shall be constructed of poured concrete |  |  |  |  |
| Dividers – tank divider walls and divider wall supports should be constructed of heavy durable plastic, fiberglass concrete or other similar corrosion resistant materials |  |  |  |  |
| Inlet and outlet ports – constructed of schedule 40 pvc plastic sanitary tees or other similar corrosion resistant material |  |  |  |  |
| Wall thickness meets minimum standard – See 69.5 (5) (6) (7) (8) & (9) |  |  |  |  |
| Bedding – fiberglass or plastic tanks shall be bedded according to manufacturer’s specifications. Prevent flotation |  |  |  |  |

# Construction Inspection – Connecting Pipes

| Description | Not Applicable | Meets Standard | Does Not Meet Standard | Notes |
| --- | --- | --- | --- | --- |
| Minimum diameter – 4” diameter schedule 40 for at least the first 5 feet |  |  |  |  |
| Tank connections – shall be made by self-sealing gaskets cast into the concrete or formed into the plastic or fiberglass |  |  |  |  |
| Joints – shall be approved plastic pipe connections such as solvent-welded or compression type gaskets |  |  |  |  |
| Pipe in unstable ground – schedule 40 plastic pipe shall be used extending across excavations or unstable ground to at least 2 feet beyond the point where original ground has not been disturbed |  |  |  |  |

# Construction Inspection – Secondary Treatment

| Description | Not Applicable | Meets Standard | Does Not Meet Standard | Notes |
| --- | --- | --- | --- | --- |
| Vertical separation from seasonal high groundwater no less than 3’ |  |  |  |  |
| Percolation Test |  |  |  |  |
| Soil Survey |  |  |  |  |
| Confining layer determination – groundwater level and rock formations |  |  |  |  |
| Site limitations |  |  |  |  |
| Prohibited drainage – Roof, foundation and storm drains shall not discharge into or upon subsurface absorption systems |  |  |  |  |
| Prohibited construction – No construction of any kind shall cover the septic tank, distribution box or absorption field |  |  |  |  |
| Driveway crossings – Lines under driveways shall be constructed of schedule 40 plastic pipe and shall be protected from freezing |  |  |  |  |
| Easements |  |  |  |  |
| Depth – Lateral trenches shall not exceed 36 inches in depth. Not less than 6” of porous soil shall be provided over the laterals |  |  |  |  |
| Length – shall be no greater than 100’ |  |  |  |  |
| Separation Distance – 6’ of undisturbed soil shall be let between each trench edge on level sites |  |  |  |  |
| Grade – Trench bottom should be constructed level from end to end |  |  |  |  |
| Compaction – shall be minimum use on the area of the soil absorption field |  |  |  |  |
| Fill soil – soil absorption systems shall not be installed in fill soil |  |  |  |  |
| Soil smearing – soils with significant clay content should not be worked when wet |  |  |  |  |

Type of system _________________________________________________________________

Gravel Systems:  A minimum of 6 inches of clean, washed river gravel, free of clay and clay coatings, shall be laid below the distribution pipe, and enough gravel shall be used to cover the pipe.  This gravel shall be of such a size that 100 percent will pass a 2 ½” screen and 100 percent will be retained on a ¾” screen.  Limestone or crushed rock is not recommended for soil absorption systems.  Lateral trenches for gravel systems shall be a minimum of 24 inches and a maximum of 36 inches in width at the bottom of the trench.  The distribution pipes shall be laid with a minimum grade of 2 inches per 100 feet of run and a maximum grad of 6 inches per 100 feet of run, with a preference given to the lesser slope.  Distribution pipe shall be PVC rigid plastic meeting ASTM Standard 2727, or other suitable material approved by the administrative authority.  The inside diameter shall be not less than 4” with perforations at least ½” and not more than ¾” in diameter spaced no more than 40 inches apart.  Two rows of perforations shall be provided located 120 degrees apart along the bottom half of the tubing (each 60 degrees up from the bottom centerline).   The end of the pipe in each trench shall be sealed with a watertight cap.  Unbacked, rolled 3 ½ inch thick fiberglass insulation, untreated building paper, synthetic drainage fabric or other approved material shall be laid so as to separate the gravel from the soil backfill.

Gravel less Pipe Systems:  Manufacturer’s specifications and installation procedures shall be adhered to.  The 8 and 10 inch I.D. corrugated polyethylene tubing used in gravel less systems shall meet the requirements of ASTM F667.  Two row of perforation shall be located 120 degrees apart along the bottom half of the tubing (each 60 degrees up from he bottom centerline).  Perforations shall be cleanly cut into each inner corrugation along the length of the tubing and should be staggered so that there is only one hole in each corrugation.  The tubing should be visibly marked to indicate the top of the pipe.  All gravel less drain field pipe shall b encased, at the point of manufacture, with a geotextile filter wrap specific to this purpose.  If dug with a backhoe, the minimum trench width for the gravel less system shall be 18 inches in sandy loam soil to ensure proper backfill around the bottom half of the pipe.  In clay soils, the minimum trench width shall be 24 inches.  If the pipe is laid in with a wheel trencher leaving a curved trench bottom the trench width may be just 2 inches wider than the outside diameter of the pipe.  An increase of 20 percent in total length shall be required if 8 inch tubing is used rather than 10 inch.

Notes ________________________________________________________________________ ______________________________________________________________________________

____________________________________________________________________________________________________________________________________________________________